# Section 7.	Technical Specifications

Procurement of Industrial Filter (Coalescer Filter) for 450MW CCPP-North plant of APSCL

| Sl. | Filter Type | Description of Item | Requirement | Quantity |
| --- | --- | --- | --- | --- |
|  | 1st Stage Filter (Coalescer Filter) | Name of Manufacturer | (To be mentioned) | 3240 (Three thousand two hundred forty) Pcs. 1st Stage filter (Coalescer filter) (06 sets) |
|  |  | Country of origin (where materials grown) | EU / G7 |  |
|  |  | Filter Class to EN 779:2012 | G4 |  |
|  |  | Fire class as per DIN 53438 | F1 |  |
|  |  | Filter Type | Washable, metal-free, non-corroding, leak-free construction and exposed to constant water spray or fogging. |  |
|  |  | Filter Media | Non-woven synthetic media with water repellency or hydrophobic characteristics |  |
|  |  | Frame Dimension | 592×592×96 mm |  |
|  |  | Frame | ABS or Polystyrene Plastic |  |
|  |  | Frame Stabilizer | ABS or Polystyrene Plastic |  |
|  |  | Gasket | At least 5 mm gasket (on each reciprocal vertical non-flow side) |  |
|  |  | Sealant | Polyurethane |  |
|  |  | Pleat Separator | hot-melt support or casted support |  |
|  |  | Filtering Area | Minimum 2.0 m2 |  |
|  |  | Initial pressure drop at 4250 m³/h (New Filter) | ≤ 85 Pa |  |
|  |  | Recom. Final pressure drop at 4250 m³/h (Soiled Filter) | ≥ 250 Pa |  |
|  |  | Burst pressure drop | ≥ 2000 Pa |  |
|  |  | Maximum Operating temperature | ≥ 68 °C |  |
|  |  | Moisture-resistance (rel. humidity) | 100 % |  |
|  |  | Flow-rate per element (as per EN779:2012) | 4250 m³/h |  |
|  |  | Average arrestance | >90 % |  |

Terms & Conditions:

1.	Tenderer must submit original Printed Catalogue from the manufacturer including products description/technical specification along with the offer.

2.	Tenderer must submit End-User Certificate mentioning that manufacturer’s filters were used in Gas Turbine Model:SGT2000E or SGT4000F/Formerly Model:V94.3A and performance of the filters were satisfactory for minimum one (01) year. End-User Name, address, phone no, fax no, email address etc. must be mentioned in End-User’s official pad.

3.	Tenderer/Supplier must submit the following Third-Party Test Report as per EN779:2012 from independent Standard Testing Laboratory for each filter stage during bid documents submission.

a. Arrestance (%) Vs Dust Feed, (gm)

b. initial Pressure Drop (Pa) Vs Air Flow Rate (m3/h) at 25% to 100% of nominal air flow and Final Pressure Drop (Pa) Vs Nominal Air Flow Rate (m3/h)

4.	The test reports should be original one. If photocopy of test report is submitted that should be certified by Notary Public.

5.	Tenderer/Supplier must provide Original Filter Manufacturer’s authorization letter to confirm that the offer originated from original filter Manufacturer. Authorization letter from dealer will not be accepted. Trading house will not be accepted if not supported by manufacturer’s Authorization Letter. Authorization letter from manufacturer’s Sales office located in other country (not in the country of origin) may be allowed if supported by manufacturer’s letter in this regard.

6.	Manufacturer should have proven experience to supply proposed filters at least one time to Gas Turbine Model:SGT4000F/Formerly Model:V94.3A or SGT2000E and provide that proofness with purchase order copy should be attached with tender.

7.	One-piece filter must be submitted as sample during bid documents submission. Submitted sample physical verification test will be considered during evaluation.

8.	Country of origin: European Union (EU)/G7. Certificate of origin issued by Chamber of commerce or government authority, shall be submitted during delivery of the material.

N.B.: Tendered/Supplier can visit site area for assessment of site condition before quoting price (if required)