# Section 7.	Technical Specifications

Procurement of Industrial Filter (Pre Filter) for 450MW CCPP-North plant

of APSCL

| Sl. | Filter Type | Description of Item | Requirement | Quantity |
| --- | --- | --- | --- | --- |
|  | 2nd Stage Filter (Pre-Filter) | Country of origin | EU, G7 | 2700 (Two thousand seven hundred) Pcs. 2nd Stage filter (Pre-filter) |
|  |  | Filter class to EN 779:2012 | M6 |  |
|  |  | Fire class as per DIN 53438 | F1 |  |
|  |  | Filter Type | Mist eliminator type |  |
|  |  | Materials | High-performance, nonwoven, tear-resistant synthetic organic fibers. |  |
|  |  | Dimensions | 592 x 592 x 600-650 mm |  |
|  |  | Frame | Filter pockets are foamed-in polyurethane front frame, Frame width 25 mm |  |
|  |  | Gasket | 5 mm continuous polyurethane gasket as per mounting arrangement |  |
|  |  | No. of pockets | 5-10 |  |
|  |  | Filtering area | ≥3.5 m² |  |
|  |  | Initial pressure drop | ≤40 Pa |  |
|  |  | Recommended final pressure drop | ≤450 Pa |  |
|  |  | Burst pressure drop | ≥2000 Pa |  |
|  |  | Max. operating temperature | ≥70 °C |  |
|  |  | Relative humidity | Up to 100 % |  |
|  |  | Flow-rate per element (as per EN779: 2012) | ≥3400 m³/h |  |
|  |  | Microbiologically inactive. | Yes |  |
|  |  | Efficiency (as per EN779:2012) | ≥60 |  |

N.B.:

i) 	All the pages of the tender document as well as all the attached documents 	shall be signed & Sealed by the Signatory authority on behalf of the Tenderer.

ii)	Original Catalogue from the manufacturer including products	description/ 	technical specifications shall be submitted with tender.

iii) Name of the manufacturer and the country of origin of the offered equipment/ 	items must be mentioned in tender.

iv)	The tenderer must submit at least one (1) experience certificate issued by the 	End-User regarding supplying of Electrical/Mechanical/Similar goods worth 	not less than equivalent taka eleven million under a single contract pursuant to 	ITT Clause 14.1 (b).

v) 	If the tenderer is not Manufacturer; the tenderer must submit 	“Authorization letter” issued by the Filter Manufacturer confirming that the 	offered filters are originated from original filter Manufacturer. 	Authorization letter from dealer will not be accepted. Trading house will not 	be accepted if not supported by manufacturer's Authorization Letter. 	Authorization Letter from manufacturer's Sales office located in other 	country (not in the country of origin) may be allowed if supported by 	manufacturer's letter in this regard.

vi) 	Manufacturer’s experience certificate issued by the End user regarding 	supply of offered Air Intake Pre filter that were used in Siemens model 	SGT-4000F or Formerly Model: V94.3A or SGT 2000E Gas Turbine, should be 	submitted with tender (at least one). The End-User performance certificate 	should also confirm that the performance of the filters were satisfactory for 	minimum one (01) year.

End-User Name, address, phone no, fax no, email address etc. must be 	mentioned in End-User's official pad.

vii) 	Tenderer must submit with tender, the following third party Test report as 		per EN779:2012 from Independent standard testing laboratory.

a) Efficiency (%) Vs Dust Feed, (gm)

b) Initial Pressure Drop (Pa) Vs Air Flow Rate (m3/h) at 25% to 125% of 			nominal air flow and Final Pressure Drop (Pa) Vs Air Flow Rate (m3/h)

c) Collection Efficiency (%) Vs Particle Size (´m) [Efficiency after different 		dust loading phases].

The test reports should be original one. If photocopy of test report is 			submitted, that should be certified by Notary Public.

viii) One piece of offered Pre filter must be submitted with tender as sample. 	Tender without Sample shall be treated as Non-Responsive.

ix)	In case of any mismatch of materials/size detected, the supplier shall have to 	take back the mismatched items at their own cost and replace the same with 	appropriate items without claim of additional cost to the purchaser.

x)	The warranty of the supplied filters shall be minimum 5000 hours (service life 	time) after installation or eighteen (18) months from the date of delivery at 	APSCL Site. The validity of the performance security shall be extended 	accordingly.

xi)	During delivery of the materials, the supplier shall have to submit certificate 	of origin issued by chamber of commerce or gov’t authority of the 	manufacturing country.

xii)	Manufacturer’s warranty certificate stating quality, quantity and genuineness 	of goods shall be submitted during delivery of the materials.